## Sheet1
To calculate Rcurve and LCurve from R and X from Equation 30 (p69) of ENA G5/5 for use in OpenDSS
These are used in the Reactor component to calculate Zh (frequency dependant impedence) | [8 empty] | 1 EV |  | 20 EVs |  | No harmonic impedence |  |  | R | X | Z
|  |  |  | L=X/2piF |  |  |  |  | From Opendss | Calculated | From Opendss | Calculated | From Opendss | Calculated |  | 0.0212 | 0.0217 | 0.030337
k | h |  | R | X | L | L(pu) | VS | Z | I | V | I | V | I | V | old |  | R in Zeq | X in Zeq |  | Z confirmed | R p.u | L from Xeq | Confirmed | X from L | X p.u | Z | Zp.u | Correct Zpu
1 | 1 | 50 | 1 | 1 | 0.0031831 | 1 | 230 | 0.030337 | 26.994 | 229.1811 | 162.081 | 225.083 | 125.356 | 226.1971 | 0.030337 | 1 | 0.0212 | 0.0217 | 0.0217 | 0.030337 | 1 | 6.9073e-05 | 1 | 314.1593 | 1 | 0.030337 | 1 | 1
1 | 2 | 100 | 1.4142 | 2 | 0.0031831 | 1 | 0 | 0.052749 | 0.015859 | -0.00083655 | 0.042758 | -0.0022554 | 0.028529 | -0.00086549 | 0.060674 | 1.7388 | 0.029981 | 0.0434 | 0.0434 | 0.052749 | 1.4142 | 6.9073e-05 | 1 | 628.3185 | 2 | 0.052749 | 1.7388 | 1.7388
1 | 3 | 150 | 1.7321 | 3 | 0.0031831 | 1 | 0 | 0.074742 | 0.27999 | -0.020927 | 2.727 | -0.20382 | 1.8226 | -0.055293 | 0.091011 | 2.4637 | 0.036719 | 0.0651 | 0.0651 | 0.074742 | 1.7321 | 6.9073e-05 | 1 | 942.4778 | 3 | 0.074742 | 2.4637 | 2.4637
1 | 4 | 200 | 2 | 4 | 0.0031831 | 1 | 0 | 0.096602 | 0.012838 | -0.0012402 | 0.043958 | -0.0042464 | 0.029568 | -0.00089699 | 0.12135 | 3.1843 | 0.0424 | 0.0868 | 0.0868 | 0.096602 | 2 | 6.9073e-05 | 1 | 1256.6371 | 4 | 0.096602 | 3.1843 | 3.1843
1 | 5 | 250 | 2.2361 | 5 | 0.0031831 | 1 | 0 | 0.1184 | 0.23081 | -0.027328 | 2.7388 | -0.32428 | 1.8598 | -0.056421 | 0.15168 | 3.903 | 0.047405 | 0.1085 | 0.1085 | 0.1184 | 2.2361 | 6.9073e-05 | 1 | 1570.7963 | 5 | 0.1184 | 3.903 | 3.903
1 | 6 | 300 | 2.4495 | 6 | 0.0031831 | 1 | 0 | 0.14017 | 0.010837 | -0.001519 | 0.025648 | -0.0035952 | 0.017708 | -0.00053721 | 0.18202 | 4.6206 | 0.051929 | 0.1302 | 0.1302 | 0.14017 | 2.4495 | 6.9073e-05 | 1 | 1884.9556 | 6 | 0.14017 | 4.6206 | 4.6206
1 | 7 | 350 | 2.6458 | 7 | 0.0031831 | 1 | 0 | 0.16192 | 0.26271 | -0.042539 | 1.3986 | -0.22647 | 0.98981 | -0.030028 | 0.21236 | 5.3376 | 0.05609 | 0.1519 | 0.1519 | 0.16192 | 2.6458 | 6.9073e-05 | 1 | 2199.1149 | 7 | 0.16192 | 5.3376 | 5.3376
0.5 | 8 | 400 | 2.8284 | 4 | 0.0015915 | 0.5 | 0 | 0.1055 | 0.01081 | -0.0011405 | 0.016795 | -0.0017718 | 0.012203 | -0.00037021 | 0.12135 | 3.4775 | 0.059963 | 0.0868 | 0.0868 | 0.1055 | 2.8284 | 3.4537e-05 | 0.5 | 1256.6371 | 4 | 0.1055 | 3.4775 | 3.4775
0.5 | 9 | 450 | 3 | 4.5 | 0.0015915 | 0.5 | 0 | 0.11654 | 0.03141 | -0.0036604 | 1.0447 | -0.12175 | 0.79024 | -0.023974 | 0.13652 | 3.8414 | 0.0636 | 0.09765 | 0.09765 | 0.11654 | 3 | 3.4537e-05 | 0.5 | 1413.7167 | 4.5 | 0.11654 | 3.8414 | 3.8414
0.5 | 10 | 500 | 3.1623 | 5 | 0.0015915 | 0.5 | 0 | 0.12754 | 0.007843 | -0.0010003 | 0.0094901 | -0.0012104 | 0.0075264 | -0.00022833 | 0.15168 | 4.2041 | 0.06704 | 0.1085 | 0.1085 | 0.12754 | 3.1623 | 3.4537e-05 | 0.5 | 1570.7963 | 5 | 0.12754 | 4.2041 | 4.2041
0.5 | 11 | 550 | 3.3166 | 5.5 | 0.0015915 | 0.5 | 0 | 0.13852 | 0.22535 | -0.031216 | 0.41287 | -0.057191 | 0.34504 | -0.010467 | 0.16685 | 4.5661 | 0.070312 | 0.11935 | 0.11935 | 0.13852 | 3.3166 | 3.4537e-05 | 0.5 | 1727.876 | 5.5 | 0.13852 | 4.5661 | 4.5661
0.5 | 13 | 650 | 3.6056 | 6.5 | 0.0015915 | 0.5 | 0 | 0.16043 | 0.081173 | -0.013023 | 0.35064 | -0.056253 | 0.33291 | -0.0101 | 0.19719 | 5.2883 | 0.076438 | 0.14105 | 0.14105 | 0.16043 | 3.6056 | 3.4537e-05 | 0.5 | 2042.0352 | 6.5 | 0.16043 | 5.2883 | 5.2883
0.5 | 15 | 750 | 3.873 | 7.5 | 0.0015915 | 0.5 | 0 | 0.18229 | 0.10836 | -0.019753 | 0.095224 | -0.017358 | 0.10623 | -0.0032228 | 0.22753 | 6.0088 | 0.082107 | 0.16275 | 0.16275 | 0.18229 | 3.873 | 3.4537e-05 | 0.5 | 2356.1945 | 7.5 | 0.18229 | 6.0088 | 6.0088
0.5 | 17 | 850 | 4.1231 | 8.5 | 0.0015915 | 0.5 | 0 | 0.20411 | 0.044851 | -0.0091548 | 0.08274 | -0.016888 | 0.11194 | -0.003396 | 0.25786 | 6.7282 | 0.08741 | 0.18445 | 0.18445 | 0.20411 | 4.1231 | 3.4537e-05 | 0.5 | 2670.3538 | 8.5 | 0.20411 | 6.7282 | 6.7282
0.5 | 19 | 950 | 4.3589 | 9.5 | 0.0015915 | 0.5 | 0 | 0.22591 | 0.099272 | -0.022427 | 0.058999 | -0.013329 | 0.098087 | -0.0029757 | 0.2882 | 7.4468 | 0.092409 | 0.20615 | 0.20615 | 0.22591 | 4.3589 | 3.4537e-05 | 0.5 | 2984.513 | 9.5 | 0.22591 | 7.4468 | 7.4468
0.5 | 21 | 1050 | 4.5826 | 10.5 | 0.0015915 | 0.5 | 0 | 0.2477 | 0.044716 | -0.011076 | 0.033608 | -0.0083245 | 0.066815 | -0.002027 | 0.31854 | 8.1649 | 0.097151 | 0.22785 | 0.22785 | 0.2477 | 4.5826 | 3.4537e-05 | 0.5 | 3298.6723 | 10.5 | 0.2477 | 8.1649 | 8.1649
0.5 | 23 | 1150 | 4.7958 | 11.5 | 0.0015915 | 0.5 | 0 | 0.26947 | 0.055341 | -0.014913 | 0.03779 | -0.010183 | 0.083876 | -0.0025445 | 0.34887 | 8.8825 | 0.10167 | 0.24955 | 0.24955 | 0.26947 | 4.7958 | 3.4537e-05 | 0.5 | 3612.8316 | 11.5 | 0.26947 | 8.8825 | 8.8825
0.5 | 25 | 1250 | 5 | 12.5 | 0.0015915 | 0.5 | 0 | 0.29123 | 0.060123 | -0.017509 | 0.033136 | -0.0096501 | 0.074602 | -0.0022632 | 0.37921 | 9.5997 | 0.106 | 0.27125 | 0.27125 | 0.29123 | 5 | 3.4537e-05 | 0.5 | 3926.9908 | 12.5 | 0.29123 | 9.5997 | 9.5997
0.5 | 27 | 1350 | 5.1962 | 13.5 | 0.0015915 | 0.5 | 0 | 0.31298 | 0.033899 | -0.01061 | 0.032454 | -0.010157 | 0.068187 | -0.0020686 | 0.40955 | 10.3167 | 0.11016 | 0.29295 | 0.29295 | 0.31298 | 5.1962 | 3.4537e-05 | 0.5 | 4241.1501 | 13.5 | 0.31298 | 10.3167 | 10.3167
0.5 | 29 | 1450 | 5.3852 | 14.5 | 0.0015915 | 0.5 | 0 | 0.33472 | 0.05514 | -0.018457 | 0.047006 | -0.015734 | 0.088221 | -0.0026763 | 0.43989 | 11.0335 | 0.11417 | 0.31465 | 0.31465 | 0.33472 | 5.3852 | 3.4537e-05 | 0.5 | 4555.3093 | 14.5 | 0.33472 | 11.0335 | 11.0335
0.5 | 31 | 1550 | 5.5678 | 15.5 | 0.0015915 | 0.5 | 0 | 0.35646 | 0.064736 | -0.023076 | 0.05026 | -0.017916 | 0.08345 | -0.0025316 | 0.47022 | 11.75 | 0.11804 | 0.33635 | 0.33635 | 0.35646 | 5.5678 | 3.4537e-05 | 0.5 | 4869.4686 | 15.5 | 0.35646 | 11.75 | 11.75
0.5 | 33 | 1650 | 5.7446 | 16.5 | 0.0015915 | 0.5 | 0 | 0.37819 | 0.036693 | -0.013877 | 0.050894 | -0.019248 | 0.075045 | -0.0022766 | 0.50056 | 12.4665 | 0.12178 | 0.35805 | 0.35805 | 0.37819 | 5.7446 | 3.4537e-05 | 0.5 | 5183.6279 | 16.5 | 0.37819 | 12.4665 | 12.4665
0.5 | 35 | 1750 | 5.9161 | 17.5 | 0.0015915 | 0.5 | 0 | 0.39993 | 0.066547 | -0.026614 | 0.070622 | -0.028244 | 0.09312 | -0.002825 | 0.5309 | 13.1828 | 0.12542 | 0.37975 | 0.37975 | 0.39993 | 5.9161 | 3.4537e-05 | 0.5 | 5497.7871 | 17.5 | 0.39993 | 13.1828 | 13.1828
0.5 | 37 | 1850 | 6.0828 | 18.5 | 0.0015915 | 0.5 | 0 | 0.42165 | 0.033715 | -0.014216 | 0.069085 | -0.02913 | 0.081769 | -0.0024806 | 0.56123 | 13.899 | 0.12895 | 0.40145 | 0.40145 | 0.42165 | 6.0828 | 3.4537e-05 | 0.5 | 5811.9464 | 18.5 | 0.42165 | 13.899 | 13.899
0.5 | 39 | 1950 | 6.245 | 19.5 | 0.0015915 | 0.5 | 0 | 0.44338 | 0.018291 | -0.0081099 | 0.066055 | -0.029287 | 0.070287 | -0.0021323 | 0.59157 | 14.6151 | 0.13239 | 0.42315 | 0.42315 | 0.44338 | 6.245 | 3.4537e-05 | 0.5 | 6126.1057 | 19.5 | 0.44338 | 14.6151 | 14.6151
0.5 | 41 | 2050 | 6.4031 | 20.5 | 0.0015915 | 0.5 | 0 | 0.4651 | 0.036538 | -0.016994 | 0.07262 | -0.033776 | 0.069652 | -0.002113 | 0.62191 | 15.3312 | 0.13575 | 0.44485 | 0.44485 | 0.4651 | 6.4031 | 3.4537e-05 | 0.5 | 6440.2649 | 20.5 | 0.4651 | 15.3312 | 15.3312
0.5 | 43 | 2150 | 6.5574 | 21.5 | 0.0015915 | 0.5 | 0 | 0.48682 | 0.030731 | -0.014961 | 0.073527 | -0.035794 | 0.063677 | -0.0019318 | 0.65224 | 16.0471 | 0.13902 | 0.46655 | 0.46655 | 0.48682 | 6.5574 | 3.4537e-05 | 0.5 | 6754.4242 | 21.5 | 0.48682 | 16.0471 | 16.0471
0.5 | 45 | 2250 | 6.7082 | 22.5 | 0.0015915 | 0.5 | 0 | 0.50854 | 0.018236 | -0.0092735 | 0.067724 | -0.03444 | 0.053056 | -0.0016096 | 0.68258 | 16.7631 | 0.14221 | 0.48825 | 0.48825 | 0.50854 | 6.7082 | 3.4537e-05 | 0.5 | 7068.5835 | 22.5 | 0.50854 | 16.7631 | 16.7631
0.5 | 47 | 2350 | 6.8557 | 23.5 | 0.0015915 | 0.5 | 0 | 0.53026 | 0.028758 | -0.015249 | 0.090136 | -0.047795 | 0.064156 | -0.0019463 | 0.71292 | 17.4789 | 0.14534 | 0.50995 | 0.50995 | 0.53026 | 6.8557 | 3.4537e-05 | 0.5 | 7382.7427 | 23.5 | 0.53026 | 17.4789 | 17.4789
0.5 | 49 | 2450 | 7 | 24.5 | 0.0015915 | 0.5 | 0 | 0.55197 | 0.028741 | -0.015864 | 0.079569 | -0.04392 | 0.051546 | -0.0015638 | 0.74326 | 18.1948 | 0.1484 | 0.53165 | 0.53165 | 0.55197 | 7 | 3.4537e-05 | 0.5 | 7696.902 | 24.5 | 0.55197 | 18.1948 | 18.1948