## Sheet1
To calculate Rcurve and LCurve from R and X from Equation 30 (p69) of ENA G5/5 for use in OpenDSS
These are used in the Reactor component to calculate Zh (frequency dependant impedence) | [8 empty] | 1 EV |  | 20 EVs |  | No harmonic impedence |  |  | R | X | Z
|  |  |  | L=X/2piF |  |  |  |  | From Opendss | Calculated | From Opendss | Calculated | From Opendss | Calculated |  | 0.053 | 0.009 | 0.053759
k | h |  | R | X | L | L(pu) | VS | Z | I | V | I | V | I | V | old
1 | 1 | 50 | 1 | 1 | 0.0031831 | 1 | 230 | 0.053759 | 26.994 | 228.5488 | 162.081 | 221.2867 | 125.356 | 223.261 | 0.053759
1 | 2 | 100 | 1.4142 | 2 | 0.0031831 | 1 | 0 | 0.077084 | 0.015859 | -0.0012225 | 0.042758 | -0.003296 | 0.028529 | -0.0015337 | 0.10752
1 | 3 | 150 | 1.7321 | 3 | 0.0031831 | 1 | 0 | 0.095687 | 0.27999 | -0.026792 | 2.727 | -0.26093 | 1.8226 | -0.097982 | 0.16128
1 | 4 | 200 | 2 | 4 | 0.0031831 | 1 | 0 | 0.11195 | 0.012838 | -0.0014372 | 0.043958 | -0.0049209 | 0.029568 | -0.0015895 | 0.21503
1 | 5 | 250 | 2.2361 | 5 | 0.0031831 | 1 | 0 | 0.12677 | 0.23081 | -0.029259 | 2.7388 | -0.34719 | 1.8598 | -0.099982 | 0.26879
1 | 6 | 300 | 2.4495 | 6 | 0.0031831 | 1 | 0 | 0.14061 | 0.010837 | -0.0015237 | 0.025648 | -0.0036062 | 0.017708 | -0.00095196 | 0.32255
1 | 7 | 350 | 2.6458 | 7 | 0.0031831 | 1 | 0 | 0.15373 | 0.26271 | -0.040386 | 1.3986 | -0.215 | 0.98981 | -0.053211 | 0.37631
0.5 | 8 | 400 | 2.8284 | 4 | 0.0015915 | 0.5 | 0 | 0.15417 | 0.01081 | -0.0016666 | 0.016795 | -0.0025892 | 0.012203 | -0.00065603 | 0.21503
0.5 | 9 | 450 | 3 | 4.5 | 0.0015915 | 0.5 | 0 | 0.16408 | 0.03141 | -0.0051537 | 1.0447 | -0.17141 | 0.79024 | -0.042482 | 0.24191
0.5 | 10 | 500 | 3.1623 | 5 | 0.0015915 | 0.5 | 0 | 0.17354 | 0.007843 | -0.001361 | 0.0094901 | -0.0016469 | 0.0075264 | -0.00040461 | 0.26879
0.5 | 11 | 550 | 3.3166 | 5.5 | 0.0015915 | 0.5 | 0 | 0.18262 | 0.22535 | -0.041153 | 0.41287 | -0.075397 | 0.34504 | -0.018549 | 0.29567
0.5 | 13 | 650 | 3.6056 | 6.5 | 0.0015915 | 0.5 | 0 | 0.19985 | 0.081173 | -0.016222 | 0.35064 | -0.070074 | 0.33291 | -0.017897 | 0.34943
0.5 | 15 | 750 | 3.873 | 7.5 | 0.0015915 | 0.5 | 0 | 0.21608 | 0.10836 | -0.023415 | 0.095224 | -0.020576 | 0.10623 | -0.005711 | 0.40319
0.5 | 17 | 850 | 4.1231 | 8.5 | 0.0015915 | 0.5 | 0 | 0.23153 | 0.044851 | -0.010384 | 0.08274 | -0.019157 | 0.11194 | -0.0060179 | 0.45695
0.5 | 19 | 950 | 4.3589 | 9.5 | 0.0015915 | 0.5 | 0 | 0.24634 | 0.099272 | -0.024454 | 0.058999 | -0.014534 | 0.098087 | -0.005273 | 0.51071
0.5 | 21 | 1050 | 4.5826 | 10.5 | 0.0015915 | 0.5 | 0 | 0.26061 | 0.044716 | -0.011653 | 0.033608 | -0.0087586 | 0.066815 | -0.0035919 | 0.56447
0.5 | 23 | 1150 | 4.7958 | 11.5 | 0.0015915 | 0.5 | 0 | 0.27444 | 0.055341 | -0.015188 | 0.03779 | -0.010371 | 0.083876 | -0.004509 | 0.61823
0.5 | 25 | 1250 | 5 | 12.5 | 0.0015915 | 0.5 | 0 | 0.28789 | 0.060123 | -0.017309 | 0.033136 | -0.0095396 | 0.074602 | -0.0040105 | 0.67198
0.5 | 27 | 1350 | 5.1962 | 13.5 | 0.0015915 | 0.5 | 0 | 0.30101 | 0.033899 | -0.010204 | 0.032454 | -0.0097689 | 0.068187 | -0.0036656 | 0.72574
0.5 | 29 | 1450 | 5.3852 | 14.5 | 0.0015915 | 0.5 | 0 | 0.31383 | 0.05514 | -0.017305 | 0.047006 | -0.014752 | 0.088221 | -0.0047426 | 0.7795
0.5 | 31 | 1550 | 5.5678 | 15.5 | 0.0015915 | 0.5 | 0 | 0.3264 | 0.064736 | -0.02113 | 0.05026 | -0.016405 | 0.08345 | -0.0044862 | 0.83326
0.5 | 33 | 1650 | 5.7446 | 16.5 | 0.0015915 | 0.5 | 0 | 0.33875 | 0.036693 | -0.01243 | 0.050894 | -0.01724 | 0.075045 | -0.0040343 | 0.88702
0.5 | 35 | 1750 | 5.9161 | 17.5 | 0.0015915 | 0.5 | 0 | 0.35089 | 0.066547 | -0.02335 | 0.070622 | -0.02478 | 0.09312 | -0.005006 | 0.94078
0.5 | 37 | 1850 | 6.0828 | 18.5 | 0.0015915 | 0.5 | 0 | 0.36284 | 0.033715 | -0.012233 | 0.069085 | -0.025067 | 0.081769 | -0.0043958 | 0.99454
0.5 | 39 | 1950 | 6.245 | 19.5 | 0.0015915 | 0.5 | 0 | 0.37463 | 0.018291 | -0.0068525 | 0.066055 | -0.024747 | 0.070287 | -0.0037785 | 1.0483
0.5 | 41 | 2050 | 6.4031 | 20.5 | 0.0015915 | 0.5 | 0 | 0.38628 | 0.036538 | -0.014114 | 0.07262 | -0.028051 | 0.069652 | -0.0037444 | 1.1021
0.5 | 43 | 2150 | 6.5574 | 21.5 | 0.0015915 | 0.5 | 0 | 0.39778 | 0.030731 | -0.012224 | 0.073527 | -0.029248 | 0.063677 | -0.0034232 | 1.1558
0.5 | 45 | 2250 | 6.7082 | 22.5 | 0.0015915 | 0.5 | 0 | 0.40916 | 0.018236 | -0.0074613 | 0.067724 | -0.02771 | 0.053056 | -0.0028522 | 1.2096
0.5 | 47 | 2350 | 6.8557 | 23.5 | 0.0015915 | 0.5 | 0 | 0.42042 | 0.028758 | -0.012091 | 0.090136 | -0.037895 | 0.064156 | -0.003449 | 1.2633
0.5 | 49 | 2450 | 7 | 24.5 | 0.0015915 | 0.5 | 0 | 0.43158 | 0.028741 | -0.012404 | 0.079569 | -0.03434 | 0.051546 | -0.0027711 | 1.3171